## MicroBlue
Product Name | Product Category | Product code/s | Air Conditioning Unit size (Kilowatt) | Performance |  |  | Pump Dimensions (MM) (Without cable and tubing) |  |  | Pump BOXED (MM) |  |  | Power lead length (Metres) | Alarm lead length (Metres) | Alarm Type | Pump Weight (Grams) | Boxed Weight (Grams) | Power Consumption | [6 empty] | Colour | Inlets | Outlets | Sound Db(A) | EAN Code/s | HS Code | Warranty | MOQ's | Pump Medium | Run Dry | Valveless | Self Priming | Pump Technology | Sensing compatability | Ideal for | Approvals | [6 empty] | Compliance | Brand | Manufacturer | Country of orgin | Header Title | Product Description (Short) | Product Description (Long) | Key Features | Application | Unique Features |  |  | Webpage | Datasheet | User Manual | Schematic | Product Pictures
|  |  |  | Flow (Litres/Hour) | Head (Metres) | Lift (Metres) | Length (Millimetres) | Width (Millimetres) | Height (Millimetres) | Length (Millimetres) | Width (Millimetres) | Height (Millimetres) | [5 empty] | Voltage (V) | Frequency (Hz) | Draw (A) | Power (W) | Power (VA) | Power Factor | IPX Rating | [15 empty] | UK CA | CE | cURus | UL | Plenum | ETL | ATEX | [9 empty] | USP 1 | USP 2 | USP 3
MicroBlue® | Condensate Removal Pump | MicroBlue + Reservoir (HLA) X86-001 | 0-3.5kw | 5l/h | 5m | 2m | 150mm | 37mm | 40mm | 260mm | 150mm | 45mm | 2m | 0.5m | HLA - Audible Alarm | 226g | 440g | 110-240V | 50/60Hz | 0.13 (115V), 0.06 (240V) | 5w | 14.4VA | 0.35 | IPX4 | Blue, Grey, Orange | 6mm Barbed | 6mm Barbed | 17db(A) | MicroBlue + Reservoir (HLA) 5060194291702 | 84141025 | 3 Years | 36 | Liquid/ Condensate (Including Sediment & Bio-films) | ✅ | ✅ | ✅ | GyRok™ | CondenSense™ Reservoir (C21-001) | Cassette, Mini-split & Split systems | ✅ | ✅ | ✅ | ❌ | ✅ | ❌ | ❌ | RoHS3 (EU Directive 2011/65/EU) | BlueDiamond Pumps | Charles Austen Pumps Ltd. | United Kingdom (England) | Compact, ultra-quiet condensate removal pump - built for reliability and performance | The MicroBlue® is a compact, high-performance condensate pump with advanced diaphragm control, quiet operation, dual voltage, and a 3-year warranty—ideal for discreet, whisper quiet applications. | The MicroBlue® condensate removal pump features advanced dynamic diaphragm control and leads the microsized condensate pump market with superior performance. Its compact, anti-vibration design is ideal for conduit and discreet installations, delivering reliable, self-priming flow even in demanding high-lift applications. With dual voltage capability and a 3-year warranty, the MicroBlue sets a new benchmark for reliability and efficiency. | • Ultra-quiet in operation – 17dB(A) • Anti-vibration design and rubber mounts • Self-priming activation, no need for siphoning devices • Unique patented GyRok™ technology • Plug and play set-up for quick installation • Small, compact and lightweight | • Mini-Split systems up to 3.5KW • Ideal for bedrooms • Small offices • Libraries • Areas where sound suppression is a priority | CONDENSENSE™ RESERVOIR No more stuck float switches and regular reservoir maintenance. CondenSense™ technology uses advanced electronic sensing to intelligently detect the presence and precise level of condensate within the reservoir. This data-driven approach to condensate management enables real-time control of the MicroBlue’s operation, adjusting its performance dynamically to match the exact rate of condensate produced. | ADAPTIVE EFFICIENCY The MicroBlue®’s Adaptive Efficiency, is powered by its advanced soft start technology and variable speed control. This allows the pump to adjust seamlessly to fluctuating condensate levels, ensuring optimal performance without unnecessary energy consumption. By reducing sudden surges in operation and running only as needed, the MicroBlue® not only extends its lifespan but also promotes energy efficiency. Find out more about the CondenSense™ Reservoir here. | PERFORMANCE IN SILENCE Performing at its peak, the MicroBlue operates at just 17 dB(A), ensuring whisper-quiet performance. Its anti-vibration mounting bracket and rubberised edging minimise vibrations, making it ideal for noise-sensitive spaces like bedrooms, libraries, offices, and hospitals. With ultra-low sound and a vibration-free design, it delivers discreet, reliable operation without disruption. | https://bluediamondpump.com/microblue/ | https://bluediamondpump.com/wp-content/uploads/2025/05/MICROBLUE-Datasheet-2023.pdf | https://bluediamondpump.com/wp-content/uploads/2025/05/S30-401issue-5-MICROBLUE.pdf | https://bluediamondpump.com/wp-content/uploads/2025/05/MICROBLUE-Wiring-Diagram-UK-and-EU.pdf | https://drive.google.com/drive/folders/1XtkCt41cXvj7FsOSMd8i3nQVqkRSR1hv?usp=drive_link
|  | MicroBlue + Reservoir (FSA) X86-002 | [12 empty] | FSA - Volt Free Relay and Audible Alarm | [13 empty] | MicroBlue + Reservoir (FSA) 5060194291733 | 84141025

## MicroBlue + DK & Res
Product Name | Product Category | Product code/s | Air Conditioning Unit size (Kilowatt) | Performance |  |  | Pump Dimensions (MM) (Without cable and tubing) |  |  | Pump BOXED (MM) |  |  | Power lead length (Metres) | Alarm lead length (Metres) | Alarm Type | Ducting Kit Dimensions (MM) |  |  | Weight (Grams) | Boxed Weight (Grams) | Power Consumption | [6 empty] | Colour | Inlets | Outlets | Sound Db(A) | EAN Code/s | HS Code | Warranty | MOQ's | Pump Medium | Run Dry | Valveless | Self Priming | Pump Technology | Sensing compatability | Ideal for | Approvals | [6 empty] | Compliance | Brand | Manufacturer | Country of orgin | Header Title | Product Description (Short) | Product Description (Long) | Key Features | Application | Unique Features |  |  | Webpage | Datasheet | User Manual | Schematic | Product Pictures
|  |  |  | Flow (Litres/Hour) | Head (Metres) | Lift (Metres) | Length (Millimetres) | Width (Millimetres) | Height (Millimetres) | Length (Millimetres) | Width (Millimetres) | Height (Millimetres) |  |  |  | Length (Millimetres) | Width (Millimetres) | Height (Millimetres) |  |  | Voltage (V) | Frequency (Hz) | Draw (A) | Power (W) | Power (VA) | Power Factor | IPX Rating | [15 empty] | UK CA | CE | cURus | UL | Plenum | ETL | ATEX | [9 empty] | USP 1 | USP 2 | USP 3
MicroBlue® Ducting Kit & CondenSense™ Reservoir | Condensate Removal Pump | MicroBlue + Ducting Kit & CondenSense™ Reservoir (IVORY) X86-007 | 0-3.5kw | 5l/h | 5m | 2m | 150mm | 37mm | 40mm | 930mm | 158mm | 74mm | 2m | 0.5m | FSA - Volt Free Relay and Audible Alarm | 930mm | 140mm | 75mm | 226g | 1830g | 110-240V | 50/60Hz | 0.13 (115V), 0.06 (240V) | 5w | 14.4VA | 0.35 | IPX4 | Blue, Grey, Orange | 6mm Barbed | 6mm Barbed | 17db(A) | MicroBlue + Ducting Kit & CondenSense™ Reservoir (IVORY) 5060194291610 | 84141025 | 3 Years | 12 | Liquid/ Condensate (Including Sediment & Bio-films) | ✅ | ✅ | ✅ | GyRok™ | CondenSense™ Reservoir (C21-001) | Mini-split & Split systems | ✅ | ✅ | ✅ | ❌ | ✅ | ❌ | ❌ | RoHS3 (EU Directive 2011/65/EU) | BlueDiamond Pumps | Charles Austen Pumps Ltd. | United Kingdom (England) | Durable and discreet ducting kit designed for easy condensate pump installation | The MicroBlue Ducting Kit offers easy, discreet installation alongside your AC unit, housing a compact pump, reservoir, tubing, and cables. Available in Ivory and White, it provides a clean, professional finish and can be trimmed to fit any setup. Despite its small size, it delivers powerful performance—ideal for modern HVAC systems. | The MicroBlue Ducting Kit is engineered for easy installation and discreet integration. Designed to be mounted neatly alongside your air conditioning unit (left or right side), it houses our smallest, most compact pump along with the reservoir, tubing and cables. The ducting kit blends seamlessly into any environment, with availability in two colours; Ivory and White, offering a clean, professional finish. We understand that every AC unit installation is unique, which is why our ducting kits are designed to be easily trimmed to match your exact height requirements. Despite its small size, the MicroBlue delivers powerful condensate removal with superior performance, making the MicroBlue Ducting Kit is the ideal solution for modern HVAC systems and simplified installation. | • Ultra-quiet in operation – 17dB(A) • Anti-vibration design and rubber mounts • Self-priming activation, no need for siphoning devices • Unique patented GyRok™ technology • Plug and play set-up for quick installation • Small, compact and lightweight | • Mini-Split systems up to 3.5KW • Ideal for discreetly hiding air conditioning cables and tubing • Bedrooms • Small offices • Libraries • Areas where sound suppression is a priority | CONDENSENSE™ RESERVOIR No more stuck float switches and regular reservoir maintenance. CondenSense™ technology uses advanced electronic sensing to intelligently detect the presence and precise level of condensate within the reservoir. This data-driven approach to condensate management enables real-time control of the MicroBlue’s operation, adjusting its performance dynamically to match the exact rate of condensate produced. | ADAPTIVE EFFICIENCY The MicroBlue®’s Adaptive Efficiency, is powered by its advanced soft start technology and variable speed control. This allows the pump to adjust seamlessly to fluctuating condensate levels, ensuring optimal performance without unnecessary energy consumption. By reducing sudden surges in operation and running only as needed, the MicroBlue® not only extends its lifespan but also promotes energy efficiency. Find out more about the CondenSense™ Reservoir here. | SEAMLESS INSTALLATION Designed for a clean, professional finish, this ducting kit discreetly conceals cables, wires, and insulated tubing. It can be installed on either the left or right side of your air conditioning unit, offering flexible placement. The kit includes all necessary fixtures and fittings—screws, wall plugs, a plastic collar, and a rubber trim—ensuring a neat and secure installation. Instead of drilling large holes through walls for refrigerant lines, this kit allows you to easily route cables and tubing into the ceiling cavity, saving time and effort. | https://bluediamondpump.com/microblue-ducting-kit/ | https://bluediamondpump.com/wp-content/uploads/2025/05/MICROBLUE-AND-DUCTING-KIT-DATSHEET-UK.pdf | https://bluediamondpump.com/wp-content/uploads/2025/05/S30-619_2-MicroBlue-Ducting-Kit.pdf | https://bluediamondpump.com/wp-content/uploads/2025/05/MicroBlue-Ducting-Kit-Wiring-Diagram.pdf | https://drive.google.com/drive/folders/1XtkCt41cXvj7FsOSMd8i3nQVqkRSR1hv?usp=drive_link
|  | MicroBlue + Ducting Kit & CondenSense™ Reservoir (WHITE) X86-008 | [7 empty] | 930mm | 158mm | 74mm |  |  | FSA - Volt Free Relay and Audible Alarm |  |  |  |  | 1800g | [11 empty] | MicroBlue + Ducting Kit & CondenSense™ Reservoir (WHITE) 5060194291641 | 84141025

## MiniBlue
Product Name | Product Category | Product code/s | Air Conditioning Unit size (Kilowatt) | Performance |  |  | Pump Dimensions (MM) (Without cable and tubing) |  |  | Pump BOXED (MM) |  |  | Power lead length (Metres) | Alarm lead length (Metres) | Alarm Type | Weight (Grams) | Boxed Weight (Grams) | Power Consumption | [6 empty] | Colour | Inlets | Outlets | Sound Db(A) | EAN Code/s | HS Code | Warranty | WEEE | MOQ's | Pump Medium | Run Dry | Valveless | Self Priming | Pump Technology | Sensing compatability | Ideal for | Approvals | [6 empty] | Compliance | Brand | Manufacturer | Country of Origin | Header Title | Product Description (Short) | Product Description (Long) | Key Features | Application | Unique Features |  |  |  | Webpage | Datasheet | User Manual | Schematic | Product Pictures
|  |  |  | Flow (Litres/Hour) | Head (Metres) | Lift (Metres) | Length (Millimetres) | Width (Millimetres) | Height (Millimetres) | Length (Millimetres) | Width (Millimetres) | Height (Millimetres) | [5 empty] | Voltage (V) | Frequency (Hz) | Draw (A) | Power (W) | Power (VA) | Power Factor | IPX Rating | [16 empty] | UK CA | CE | cURus | UL | Plenum | ETL | ATEX | [9 empty] | USP 1 | USP 2 | USP 3 | USP 4
MiniBlue® | Condensate Removal Pump | MiniBlue + Continuous Running Plug (CR) X87-500 | 3.5 - 8.0kw | 8l/h | 8m | 5m | 138mm | 58mm | 67mm | 163mm | 107mm | 99mm | 2m | 0.5m | No Alarm | 644g | 670g | 240V | 50Hz | 0.03A | 5.5w | 5.7VA | 0.96 | IPX4 | Blue, Black, Grey, Orange | 8mm Straight | 8mm Straight | 21db(A) | MiniBlue + Continuous Running Plug (CR) 5060194290002 | 84141025 | 3 Years | 0 | 25 | Liquid/ Condensate (Including Sediment & Bio-films) | ✅ | ✅ | ✅ | Rotary Diaphragm | Thermistor Sensing - Temp. Sensor (S12-002) | Cassette, Mini-split & Split systems | ✅ | ✅ | ✅ | ❌ | ✅ | ❌ | ❌ | RoHS3 (EU Directive 2011/65/EU) | BlueDiamond Pumps | Charles Austen Pumps Ltd. | United Kingdom (England) | Miniaturised condensate pump engineered for low-scale domestic and light commercial applications | The MiniBlue® condensate pump delivers reliable, high-performance condensate removal for AC systems. Featuring BlueDiamond®’s patented rotary diaphragm technology, it runs quietly, handles debris-laden water, and requires minimal maintenance. Ideal for domestic and light commercial use, it ensures efficient, low-energy operation. | The MiniBlue® condensate pump is a high-performance, reliable condensate removal solution designed for efficiently removing condensed liquid from air conditioning systems. Engineered with BlueDiamond®’s exclusively patented rotary diaphragm technology, the MiniBlue pump operates quietly and offers exceptional field durability. Its self-priming capability and ability to handle debris-laden water make it the low-maintenance choice for HVAC professionals. Whether used in light commercial or domestic applications, the MiniBlue pump delivers consistent performance while ensuring minimal energy consumption and maintenance. | • Ultra-quiet in operation – 21dB(A) • Self-priming activation, no need for siphoning devices • Unique patented Rotary Diaphragm technology • Plug and play set-up for simple installation • Small, compact architecture where space is a premium | • Mini-Split systems up to 3.5-8KW • Ideal for domestic A/C systems • Small offices • Commercial/ retail stores | FLEXIBLE SENSOR OPTIONS The MiniBlue® is available with a range of sensing options, giving you the flexibility to tailor its operation to your HVAC system: CR Plug (X87-500): Converts your MiniBlue® into a continuously running pump, ideal for environments with constant condensate production. The pump activates as soon as your HVAC system is switched on, ensuring continuous drainage performance. Temperature Sensor (X87-504): Activates the pump when a 5°C temperature difference is detected between the air inlet and outlet. This ensures immediate and uninterrupted condensate removal, delivering efficient and responsive operation. *Reservoir option available with the MiniBlue R (X87-509) | OPERATES WHISPER-QUIETLY The MiniBlue pump is designed for whisper-quiet operation, making it ideal for sound-sensitive environments. Utilising BlueDiamond’s advanced rotary diaphragm technology, it minimises vibrations and sound while maintaining a reliable performance. Its efficient, valveless design ensures smooth, consistent flow with minimal maintenance, making it a top choice for straight-forward condensate removal applications. | FLEXIBLE INSTALLATION The MiniBlue pump offers flexible installation with the ability to be mounted in any orientation without affecting performance (8m/ 23ft away from the unit). Its compact design and versatile mounting options allow for seamless integration into tight spaces or unconventional setups, ensuring reliable operation across a wide range of applications. | TRUSTED RELIABILITY The MiniBlue® was the first in its class to come with a market leading 3-year warranty—proof of the confidence we have in its patented, ultra-reliable pumping technology. Every MiniBlue pump is precision-engineered and rigorously tested at our state of the art manufacturing facility meeting or exceed ISO9001 standards. From material selection to final inspection, quality is built into every step. | https://bluediamondpump.com/miniblue/ | https://bluediamondpump.com/wp-content/uploads/2025/05/MiniBlue-Datasheet-2023-UK.pdf | https://bluediamondpump.com/wp-content/uploads/2025/05/S30-194_iss_8_UK-compressed.pdf | https://bluediamondpump.com/wp-content/uploads/2025/05/Wiring-Diagrams-Mini-Maxi-Mega-UK-and-EU.pdf | https://drive.google.com/drive/folders/1CteIMqHJtGjlblMpsMSZ7ewhfnaAM0B2?usp=drive_link
|  | MicroBlue + Temperature Sensor X87-504 | [7 empty] | 163mm | 107mm | 99mm |  |  | No Alarm |  | 720g | [11 empty] | MicroBlue + Temperature Sensor 5060194290101 | 84141025

## MiniBlue R
Product Name | Product Category | Product code/s | Air Conditioning Unit size (Kilowatt) | Performance |  |  | Pump Dimensions (MM) (Without cable and tubing) |  |  | Pump BOXED (MM) |  |  | Power lead length (Metres) | Alarm lead length (Metres) | Alarm Type | Weight (Grams) | Boxed Weight (Grams) | Power Consumption | [6 empty] | Colour | Inlets | Outlets | Sound Db(A) | EAN Code/s | HS Code | Warranty | WEEE | MOQ's | Pump Medium | Run Dry | Valveless | Self Priming | Pump Technology | Sensing compatability | Ideal for | Approvals | [6 empty] | Compliance | Brand | Manufacturer | Country of origin | Header Title | Product Description (Short) | Product Description (Long) | Key Features | Application | Unique Features |  |  | Webpage | Datasheet | User Manual | Schematic | Product Pictures
|  |  |  | Flow (Litres/Hour) | Head (Metres) | Lift (Metres) | Length (Millimetres) | Width (Millimetres) | Height (Millimetres) | Length (Millimetres) | Width (Millimetres) | Height (Millimetres) | [5 empty] | Voltage (V) | Frequency (Hz) | Draw (A) | Power (W) | Power (VA) | Power Factor | IPX Rating | [16 empty] | UK CA | CE | cURus | UL | Plenum | ETL | ATEX | [9 empty] | USP 1 | USP 2 | USP 3
MiniBlue® R | Condensate Removal Pump | MiniBlue R X87-509 | 3.5 - 8.0kw | 8l/h | 8m | 5m | 138mm | 58mm | 67mm | 185mm | 122mm | 115mm | 2m | 0.5m | No Alarm | 644g | 830g | 240V | 50Hz | 0.03A | 5.5w | 5.7VA | 0.96 | IPX4 | Blue, Black, Grey, Orange | 8mm Straight | 8mm Straight | 21db(A) | MiniBlue R 5060194290149 | 84141025 | 3 Years | 0 | 25 | Liquid/ Condensate (Including Sediment & Bio-films) | ✅ | ✅ | ✅ | Rotary Diaphragm | Thermistor Sensing - Temp. Sensor (S12-002) | Cassette, Mini-split & Split systems | ✅ | ✅ | ✅ | ❌ | ✅ | ❌ | ❌ | RoHS3 (EU Directive 2011/65/EU) | BlueDiamond Pumps | Charles Austen Pumps Ltd. | United Kingdom (England) | Miniaturised condensate pump engineered for low-scale domestic and light commercial applications | The MiniBlue® R condensate pump offers reliable, high-performance removal for AC systems, featuring BlueDiamond®’s patented rotary diaphragm technology. Quiet, self-priming, and debris-tolerant, it ensures low maintenance and energy efficiency. Its forward-facing spouts provide added flexibility for easy installation in domestic or light commercial setups. | The MiniBlue® R condensate pump is a high-performance, reliable condensate removal solution designed for efficiently removing condensed liquid from air conditioning systems. Engineered with BlueDiamond®’s exclusively patented rotary diaphragm technology, the MiniBlue R pump operates quietly and offers exceptional field durability. Its self-priming capability and ability to handle debris-laden water make it the low-maintenance choice for HVAC professionals. Whether used in light commercial or domestic applications, the MiniBlue R pump delivers consistent performance while ensuring minimal energy consumption and maintenance. This unique model comes with forward facing spouts for flexible installation. | • Ultra-quiet in operation – 21dB(A) • Self-priming activation, no need for siphoning devices • Unique patented Rotary Diaphragm technology • Small, compact architecture where space is a premium • Forward facing spouts for simplified reservoir connection and installation | • Mini-Split systems up to 3.5-8KW • Ideal for domestic A/C systems • Small offices • Commercial/ retail stores • Retro fitting into old ducting kit systems | OPERATES WHISPER-QUIETLY The MiniBlue R pump is designed for whisper-quiet operation, making it ideal for sound-sensitive environments. Utilising BlueDiamond’s advanced rotary diaphragm technology, it minimises vibrations and sound while maintaining a reliable performance. Its efficient, valveless design ensures smooth, consistent flow with minimal maintenance, making it a top choice for straight-forward condensate removal applications. | FLEXIBLE INSTALLATION The MiniBlue R pump offers flexible installation with the ability to be mounted in any orientation without affecting performance (8m/ 23ft away from the unit). Its compact design, forward facing spouts and versatile mounting options allow for seamless integration into tight spaces or unconventional setups, ensuring reliable operation across a wide range of HVAC applications. | TRUSTED RELIABILITY The MiniBlue® was the first in its class to come with a market leading 3-year warranty—proof of the confidence we have in its patented, ultra-reliable pumping technology. Every MiniBlue pump is precision-engineered and rigorously tested at our state of the art manufacturing facility meeting or exceed ISO9001 standards. From material selection to final inspection, quality is built into every step. | https://bluediamondpump.com/miniblue/ | https://bluediamondpump.com/wp-content/uploads/2025/05/MiniBlue-Datasheet-2023-UK.pdf | https://bluediamondpump.com/wp-content/uploads/2025/05/S30-194_iss_8_UK-compressed.pdf | https://bluediamondpump.com/wp-content/uploads/2025/05/Wiring-Diagrams-Mini-Maxi-Mega-UK-and-EU.pdf | https://drive.google.com/drive/folders/1CteIMqHJtGjlblMpsMSZ7ewhfnaAM0B2?usp=drive_link

## MaxiBlue
Product Name | Product Category | Product code/s | Air Conditioning Unit size (Kilowatt) | Performance |  |  | Pump Dimensions (MM) (Without cable and tubing) |  |  | Pump BOXED (MM) |  |  | Power lead length (Metres) | Alarm lead length (Metres) | Alarm Type | Weight (Grams) | Boxed Weight (Grams) | Power Consumption | [6 empty] | Colour | Inlets | Outlets | Sound Db(A) | EAN Code/s | HS Code | Warranty | WEEE | MOQ's | Pump Medium | Run Dry | Valveless | Self Priming | Pump Technology | Sensing compatability | Ideal for | Approvals | [6 empty] | Compliance | Brand | Manufacturer | Country of origin | Header Title | Product Description (Short) | Product Description (Long) | Key Features | Application | Unique Features |  |  |  | Webpage | Datasheet | User Manual | Schematic | Product Pictures
|  |  |  | Flow (Litres/Hour) | Head (Metres) | Lift (Metres) | Length (Millimetres) | Width (Millimetres) | Height (Millimetres) | Length (Millimetres) | Width (Millimetres) | Height (Millimetres) | [5 empty] | Voltage (V) | Frequency (Hz) | Draw (A) | Power (W) | Power (VA) | Power Factor | IPX Rating | [16 empty] | UK CA | CE | cURus | UL | Plenum | ETL | ATEX | [9 empty] | USP 1 | USP 2 | USP 3 | USP 4
MaxiBlue® | Condensate Removal Pump | MaxiBlue + Reservoir Sensor X87-701 | 8.0 - 14.0kw | 14l/h | 8m | 8m | 157mm | 58mm | 67mm | 185mm | 122mm | 115mm | 2m | 0.5m | FSA - Volt Free Relay | 663g | 920g | 240V | 50Hz | 0.03A | 5.5w | 5.7VA | 0.96 | IPX4 | Blue, Black, Grey, Orange | 8mm Straight | 8mm Straight | 21db(A) | MaxiBlue + Reservoir Sensor (FSA) 5060194290194 | 84141025 | 3 Years | 0 | 25 | Liquid/ Condensate (Including Sediment & Bio-films) | ✅ | ✅ | ✅ | Rotary Diaphragm | Thermistor Sensing - Reservoir Sensor (C12-013) | Cassette, Mini-split & Split systems | ✅ | ✅ | ✅ | ❌ | ✅ | ❌ | ❌ | RoHS3 (EU Directive 2011/65/EU) | BlueDiamond Pumps | Charles Austen Pumps Ltd. | United Kingdom (England) | Versatile, high-performance condensate pump engineered for demanding humidity conditions | The MaxiBlue® condensate pump delivers powerful, quiet, and energy-efficient performance for mid-range AC and refrigeration systems. Featuring advanced thermistor technology and self-priming capability, it’s compact, versatile, and easy to install in any orientation—ideal for offices, hotels, and ceiling-mounted units. | The MaxiBlue® condensate pump is a high-performance solution designed for efficient and reliable condensate removal in air conditioning and refrigeration systems. Featuring advanced thermistor technology, it offers quiet operation, self-priming capability, and energy-efficient performance, making it ideal for mid-range AC units in commercial and residential settings. With its compact and versatile design, the MaxiBlue® can be installed in various orientations, ensuring flexibility even in challenging locations. Whether used in offices, hotels, or ceiling-mounted units, this pump delivers powerful, maintenance-free operation while minimising downtime and disruption. | • Quiet in operation – 21dB(A) • Mid-range condensate pump merging size and performance into one • Self-priming activation, no need for siphoning devices • Unique patented Rotary Diaphragm technology • Plug and play set-up for quick installation • Small and compact body | • Air conditioning systems up to 14KW • Mini-Split • Cassette systems • Mid-range fan coil applications • Ideal for large office blocks • Conference rooms • Retail and commercial areas • High-humidity environments | PUMPS BIOFILMS & DEBRIS WITH EASE Utilising the power of our exclusively patented rotary diaphragm technology, the MaxiBlue pump efficiently removes condensate, preventing biofilms building-up in the HVAC system, ensuring smooth, uninterrupted drainage. Its powerful pumping technology effectively clears debris and minimises blockages, reducing maintenance requirements and lowering the risk of system failure and biofilm build-up in the system. | FLEXIBLE SENSING OPTIONS The MaxiBlue® offers a variety of smart sensing options to suit different HVAC applications: Reservoir Sensor (X87-701): Uses advanced thermistor technology, eliminating the common failures of traditional float switches. Compact, silent, and maintenance-free, it reliably detects condensate even in demanding environments. DrainStik™ Sensor (X87-702): An ultra-compact, in-line sensor designed for direct installation in the drainpipe, offering precise condensate detection without interfering with drainage flow. Temperature Sensor (X87-703): Triggers the pump when a 5°C difference is detected between the air inlet and outlet, enabling immediate, uninterrupted condensate removal. | RELIABLE RESERVOIR SENSOR Remove the hassle of stuck float switches. Our advanced thermistor-based sensing technology detects temperature variations to accurately determine the presence of condensate in the reservoir. By responding to changes in thermal conductivity caused by condensate from the air conditioning unit, it offers excellent durability, and reliability compared to basic float switches. | FLEXIBLE INSTALLATION The MaxiBlue pump offers flexible installation with the ability to be mounted in any orientation without affecting performance (8m/ 23ft away from the unit). Its compact design and versatile mounting options allow for seamless integration into tight spaces or unconventional setups, ensuring reliable operation across a wide range of applications. | https://bluediamondpump.com/maxiblue/ | https://bluediamondpump.com/wp-content/uploads/2025/05/MAXIBLUE-Datasheet-2023-UK.pdf | https://bluediamondpump.com/wp-content/uploads/2025/05/S30-194_iss_8_UK-compressed.pdf | https://bluediamondpump.com/wp-content/uploads/2025/05/Wiring-Diagrams-Mini-Maxi-Mega-UK-and-EU.pdf | https://drive.google.com/drive/folders/1muXgce1z87neRSUw7O4Wb1t3EfHMuwsd?usp=drive_link
|  | MaxiBlue + DrainStik Sensor X87-702 | [7 empty] | 185mm | 122mm | 115mm |  |  | FSA - Volt Free Relay |  | 950g | [11 empty] | MaxiBlue + DrainStik Sensor (FSA) 5060194290217 | 84141025 | [7 empty] | Thermistor Sensing DrainStik (S12-004) | [11 empty] | United Kingdom (England)
|  | MaxiBlue + Temperature Sensor X87-703 | [7 empty] | 185mm | 122mm | 115mm |  |  | No Alarm |  | 870g | [11 empty] | MaxiBlue + Temperature Sensor 5060194290231 | 84141025 | [7 empty] | Thermistor Sensing - Temp. Sensor (S12-002) | [11 empty] | United Kingdom (England)

## NEW ¦ MiniBlue V2
Product Name | Product Category | Product code/s | Air Conditioning Unit size (Kilowatt) | Performance |  |  | Pump Dimensions (MM) (Without cable and tubing) |  |  | Pump BOXED (MM) |  |  | Power lead length (Metres) | Alarm lead length (Metres) | Alarm Type | Weight (Grams) | Boxed weight (Grams) | Power Consumption | [6 empty] | Colour | Inlets | Outlets | Sound Db(A) | EAN Code/s | HS Code | Warranty | WEEE | MOQ's | Pump Medium | Run Dry | Valveless | Self Priming | Pump Technology | Sensing compatability | Ideal for | Approvals | [6 empty] | Compliance | Brand | Manufacturer | Country of Origin | Header Title | Product Description (Short) | Product Description (Long) | Key Features | Application | Unique Features |  |  |  | Webpage | Datasheet | User Manual | Schematic | Product Pictures
|  |  |  | Flow (Litres/Hour) | Head (Metres) | Lift (Metres) | Length (Millimetres) | Width (Millimetres) | Height (Millimetres) | Length (Millimetres) | Width (Millimetres) | Height (Millimetres) | [5 empty] | Voltage (V) | Frequency (Hz) | Draw (A) | Power (W) | Power (VA) | Power Factor | IPX Rating | [16 empty] | UK CA | CE | cURus | UL | Plenum | ETL cus | ATEX | [9 empty] | USP 1 | USP 2 | USP 3 | USP 4
MiniBlue® ¦ V2 | Condensate Removal Pump | MiniBlue + CondenSense Reservoir X88-509 | 3.5 - 8.0kw | 8l/h | 8m | 5m | 148mm | 57mm | 74mm | 261mm | 170mm | 63mm | 2m | 2m | Volt Free Alarm, Audible Alarm & Visual LED Indicator | 640g | 810g | 115-240V | 50/60Hz | 0.03A (115v),0.05 (230V) | 5.5w | 5.7VA | 0.96 | IPX4 | Blue, Black, Grey, Orange | 8mm Straight | 8mm Straight | (Low flow) 19db(A)- (High-flow) 21db(A) | MiniBlue V2 + CondenSense Reservoir 5060194292181 | 84141025 | *3 Years | 0 | 28 | Liquid/ Condensate (Including Sediment & Bio-films) | ✅ | ✅ | ✅ | Rotary Diaphragm (Refined and enhanced) | CondenSense™ - Reservoir Sensor (C21-001) | Cassette, Mini-split & Split systems | ✅ | ✅ | ❌ | ❌ | ✅ | ✅ | ❌ | RoHS3 (EU Directive 2011/65/EU) | BlueDiamond Pumps | Charles Austen Pumps Ltd. | United Kingdom (England) | PRECISION. INTELLIGENCE. EFFICIENCY - BUILT ON A LEGACY, POWERED BY INNOVATION | MiniBlue® V2 is one of the most compact performers in the BlueDiamond® V2 Series, delivering up to 8 L/hour of condensate removal. Controlled by CondenSense™ technology with its CS2 chip, it communicates directly from reservoir to pump, providing automatic flow adjustment for whisper-quiet, energy-efficient operation. Its lightweight, filter-free design makes it the ideal choice for smaller applications where space is limited but reliability is essential. | The MiniBlue® V2 is one of the most compact and efficient performers in the BlueDiamond® V2 Series, purpose-built for reliable condensate removal in space-limited installations. Capable of delivering up to 8 L/hour, it combines powerful performance with a remarkably small footprint, making it ideal for modern, high-efficiency systems where size and simplicity matter. At the heart of the MiniBlue® V2 is advanced CondenSense™ technology featuring the intelligent CS2 microchip. This innovation enables direct communication between the reservoir and pump, allowing real-time monitoring and automatic flow adjustment. The result is whisper-quiet, energy-efficient operation that adapts seamlessly to demand while minimising wear and energy use. Its filter-free, lightweight design reduces maintenance requirements and simplifies installation, offering long-term dependability with minimal servicing. Built with the same refined architecture as the wider V2 Series, the MiniBlue® V2 benefits from integrated elastomeric feet to reduce vibration and noise, as well as streamlined plug-and-play connections for faster, cleaner setup. | • Automatic priming without the need to manually siphon. • Enhanced Rotary Diaphragm technology to prevent bio-film build-up. • Dynamic condensate monitoring for active condensate tracking and monitoring. • CondenSense™ integration for intelligent, demand-based operation with automatic flow adjustment. • Energy and sound efficiency minimises power usage and reduces operational sound. • Soft start sequencing ensures smooth, quiet system activation and prolongs pump life. | • Air conditioning systems up to 8KW. • Mini-split and cassette systems. • Low-range fan coil applications. • Ideal for pumping and preventing bio-films. | CONDENSENSE™ COMPATIBLE Now with advanced CondenSense™ technology, featuring the newly integrated CS2 microchip for intelligent automatic flow adjustment and precision soft-start sequencing delivering smarter, more efficient, and unintrusive condensate removal. | UPGRADED EFFICIENCY MiniBlue V2 features a brand new, cutting-edge brushless motor delivering unbeatable performance, superior reliability, flow control and enhanced energy efficiency. | DYNAMIC MONITORING Powered by the CS2 microchip, the system delivers real-time performance analytics directly to engineers. Rear-mounted LED indicators provide instant pump status updates, streamlining diagnostics and simplifying HVAC maintenance. | NEW ARCHITECTURE MiniBlue V2 features a new streamlined body, integrated elastomeric feet, and new plug-and-play connectivity, making setup simpler than ever. | https://bluediamondpump.com/miniblue-V2/ | https://drive.google.com/drive/folders/1aMsVxzhcZQZ0PkPIB1du6fPJMFdJfOgC?usp=drive_link | Not ready | Not ready | https://drive.google.com/drive/folders/13W3dud_yg2cOYXeOwedCiUyGV7BEXRBf?usp=drive_link

## NEW ¦ MaxiBlue V2
Product Name | Product Category | Product code/s | Air Conditioning Unit size (Kilowatt) | Performance |  |  | Pump Dimensions (MM) (Without cable and tubing) |  |  | Pump BOXED (MM) |  |  | Power lead length (Metres) | Alarm lead length (Metres) | Alarm Type | Weight (Grams) | Boxed weight (Grams) | Power Consumption | [6 empty] | Colour | Inlets | Outlets | Sound Db(A) | EAN Code/s | HS Code | Warranty | WEEE | MOQ's | Pump Medium | Run Dry | Valveless | Self Priming | Pump Technology | Sensing compatability | Ideal for | Approvals | [6 empty] | Compliance | Brand | Manufacturer | Country of Origin | Header Title | Product Description (Short) | Product Description (Long) | Key Features | Application | Unique Features |  |  |  | Webpage | Datasheet | User Manual | Schematic | Product Pictures
|  |  |  | Flow (Litres/Hour) | Head (Metres) | Lift (Metres) | Length (Millimetres) | Width (Millimetres) | Height (Millimetres) | Length (Millimetres) | Width (Millimetres) | Height (Millimetres) | [5 empty] | Voltage (V) | Frequency (Hz) | Draw (A) | Power (W) | Power (VA) | Power Factor | IPX Rating | [16 empty] | UK CA | CE | cURus | UL | Plenum | ETL cus | ATEX | [9 empty] | USP 1 | USP 2 | USP 3 | USP 4
MaxiBlue® ¦ V2 | Condensate Removal Pump | MaxiBlue + CondenSense Reservoir X88-701 | 14.0kw | 14l/h | 8m | 8m | 148mm | 57mm | 74mm | 261mm | 170mm | 63mm | 2m | 2m | Volt Free Alarm, Audible Alarm & Visual LED Indicator | 640g | 810g | 115-240V | 50/60Hz | 0.03A (115v),0.05 (230V) | 5.5w | 5.7VA | 0.96 | IPX4 | Blue, Black, Grey, Orange | 8mm Straight | 8mm Straight | (Low flow) 19db(A)- (High-flow) 21db(A) | MaxiBlue V2 + CondenSense Reservoir 5060194291979 | 84141025 | *3 Years | 0 | 28 | Liquid/ Condensate (Including Sediment & Bio-films) | ✅ | ✅ | ✅ | Rotary Diaphragm (Refined and enhanced) | CondenSense™ - Reservoir Sensor (C21-001) | Cassette, Mini-split & Split systems | ✅ | ✅ | ❌ | ❌ | ✅ | ✅ | ❌ | RoHS3 (EU Directive 2011/65/EU) | BlueDiamond Pumps | Charles Austen Pumps Ltd. | United Kingdom (England) | PERFORMANCE. INTELLIGENCE. RELIABILITY - BUILT ON A LEGACY, POWERED BY INNOVATION | MaxiBlue® V2 is the next-generation pump in the trusted BlueDiamond® range, featuring enhanced Rotary Diaphragm technology in a lighter, more efficient design. Its smart control electronics enable real-time monitoring and adaptive condensate management. With a clog-resistant, filter-free design and integrated CondenSense™ technology, it self-adjusts its flow speed to match condensate levels, ensuring precise performance, lower energy use, lower sound volumes and minimal maintenance . | MaxiBlue® V2 is the next-generation pump in the trusted BlueDiamond® range, featuring enhanced Rotary Diaphragm technology in a lighter, more efficient design. Its smart control electronics enable real-time monitoring and adaptive condensate management. With a clog-resistant, filter-free design and integrated CondenSense™ technology, it self-adjusts its flow speed to match condensate levels, ensuring precise performance, lower energy use, lower sound volumes and minimal maintenance . | • Automatic priming without the need to manually siphon. • Enhanced Rotary Diaphragm technology to prevent bio-film build-up. • Dynamic condensate monitoring for active condensate tracking and monitoring. • CondenSense™ integration for intelligent, demand-based operation with automatic flow adjustment. • Energy and sound efficiency minimises power usage and reduces operational sound. • Soft start sequencing ensures smooth, quiet system activation and prolongs pump life. | • Air conditioning systems up to 14KW. • Mini-split and cassette systems. • Mid-range fan coil applications. • High humidity environments. • Ideal for pumping and preventing bio-films. | CONDENSENSE™ COMPATIBLE Now with advanced CondenSense™ technology, featuring the newly integrated CS2 microchip for intelligent automatic flow adjustment and precision soft-start sequencing delivering smarter, more efficient, and unintrusive condensate removal. | UPGRADED EFFICIENCY MaxiBlue V2 features a brand new, cutting-edge brushless motor delivering unbeatable performance, superior reliability, flow control and enhanced energy efficiency. | DYNAMIC MONITORING Powered by the CS2 microchip, the system delivers real-time performance analytics directly to engineers. Rear-mounted LED indicators provide instant pump status updates, streamlining diagnostics and simplifying HVAC maintenance. | NEW ARCHITECTURE MaxiBlue V2 features a new streamlined body, integrated elastomeric feet, and new plug-and-play connectivity, making setup simpler than ever. | https://bluediamondpump.com/maxiblue-V2/ | https://drive.google.com/drive/folders/1WVNOezVyRuWccYGWKCB40bErEfYrN8q2?usp=drive_link | Not ready | Not ready | https://drive.google.com/drive/folders/1muXgce1z87neRSUw7O4Wb1t3EfHMuwsd?usp=drive_link

## MaxiBlue PRO
Product Name | Product Category | Product code/s | Air Conditioning Unit size (Kilowatt) | Performance |  |  | Pump Dimensions (MM) (Without cable and tubing) |  |  | Pump BOXED (MM) |  |  | Power lead length (Metres) | Alarm lead length (Metres) | Alarm Type | Weight (Grams) | Boxed weight (Grams) | Power Consumption | [6 empty] | Colour | Inlets | Outlets | Sound Db(A) | EAN Code/s | HS Code | Warranty | WEEE | MOQ's | Pump Medium | Run Dry | Valveless | Self Priming | Pump Technology | Sensing compatability | Ideal for | Approvals | [6 empty] | Compliance | Brand | Manufacturer | Country of Origin | Header Title | Product Description (Short) | Product Description (Long) | Key Features | Application | Unique Features |  |  | Webpage | Datasheet | User Manual | Schematic | Product Pictures
|  |  |  | Flow (Litres/Hour) | Head (Metres) | Lift (Metres) | Length (Millimetres) | Width (Millimetres) | Height (Millimetres) | Length (Millimetres) | Width (Millimetres) | Height (Millimetres) | [5 empty] | Voltage (V) | Frequency (Hz) | Draw (A) | Power (W) | Power (VA) | Power Factor | IPX Rating | [16 empty] | UK CA | CE | cURus | UL | Plenum | ETL | ATEX | [9 empty] | USP 1 | USP 2 | USP 3
MaxiBlue® PRO | Condensate Removal Pump | MaxiBlue + Reservoir Sensor X87-707 | 8.0 - 14.0kw | 14l/h | 8m | 8m | 157mm | 58mm | 67mm | 355mm | 345mm | 93mm | 2m | 0.5m | FSA - Volt Free Relay | 663g | 3430g | 240V | 50Hz | 0.03A | 5.5w | 5.7VA | 0.96 | IPX4 | Blue, Black, Grey, Orange | 8mm Straight | 8mm Straight | 21db(A) | MaxiBlue + Reservoir Sensor (FSA) 5060194290194 | 84141025 | 3 Years | 0 | 25 | Liquid/ Condensate (Including Sediment & Bio-films) | ✅ | ✅ | ✅ | Rotary Diaphragm | Thermistor Sensing - Reservoir Sensor (C12-013) | Cassette, Mini-split & Split systems | ✅ | ✅ | ✅ | ❌ | ✅ | ❌ | ❌ | RoHS3 (EU Directive 2011/65/EU) | BlueDiamond Pumps | Charles Austen Pumps Ltd. | United Kingdom (England) | Versatile, high-performance condensate pump engineered for demanding humidity conditions | The MaxiBlue® condensate pump delivers powerful, quiet, and energy-efficient performance for mid-range AC and refrigeration systems. Featuring advanced thermistor technology and self-priming capability, it’s compact, versatile, and easy to install in any orientation—ideal for offices, hotels, and ceiling-mounted units. | The MaxiBlue® condensate pump is a high-performance solution designed for efficient and reliable condensate removal in air conditioning and refrigeration systems. Featuring advanced thermistor technology, it offers quiet operation, self-priming capability, and energy-efficient performance, making it ideal for mid-range AC units in commercial and residential settings. With its compact and versatile design, the MaxiBlue® can be installed in various orientations, ensuring flexibility even in challenging locations. Whether used in offices, hotels, or ceiling-mounted units, this pump delivers powerful, maintenance-free operation while minimising downtime and disruption. | • Quiet in operation – 21dB(A) • Mid-range condensate pump merging size and performance into one • Self-priming activation, no need for siphoning devices • Unique patented Rotary Diaphragm technology • Plug and play set-up for quick installation • Small and compact body | • Air conditioning systems up to 14KW • Mini-Split • Cassette systems • Mid-range fan coil applications • Ideal for large office blocks • Conference rooms • Retail and commercial areas • High-humidity environments | PUMPS BIOFILMS & DEBRIS WITH EASE Utilising the power of our exclusively patented rotary diaphragm technology, the MaxiBlue pump efficiently removes condensate, preventing biofilms building-up in the HVAC system, ensuring smooth, uninterrupted drainage. Its powerful pumping technology effectively clears debris and minimises blockages, reducing maintenance requirements and lowering the risk of system failure and biofilm build-up in the system. | RELIABLE RESERVOIR SENSOR Remove the hassle of stuck float switches. Our advanced thermistor-based sensing technology detects temperature variations to accurately determine the presence of condensate in the reservoir. By responding to changes in thermal conductivity caused by condensate from the air conditioning unit, it offers excellent durability, and reliability compared to basic float switches. | FLEXIBLE INSTALLATION The MaxiBlue pump offers flexible installation with the ability to be mounted in any orientation without affecting performance (8m/ 23ft away from the unit). Its compact design and versatile mounting options allow for seamless integration into tight spaces or unconventional setups, ensuring reliable operation across a wide range of applications. | https://bluediamondpump.com/maxiblue/ | https://bluediamondpump.com/wp-content/uploads/2025/05/MAXIBLUE-Datasheet-2023-UK.pdf | https://bluediamondpump.com/wp-content/uploads/2025/05/S30-194_iss_8_UK-compressed.pdf | https://bluediamondpump.com/wp-content/uploads/2025/05/Wiring-Diagrams-Mini-Maxi-Mega-UK-and-EU.pdf | https://drive.google.com/drive/folders/1lTjfAEKyg5tXRv6333DlagxyOcdecdLd?usp=drive_link

## MegaBlue
Product Name | Product Category | Product code/s | Air Conditioning Unit size (Kilowatt) | Performance |  |  | Pump Dimensions (MM) (Without cable and tubing) |  |  | Pump BOXED (MM) |  |  | Power lead length (Metres) | Alarm lead length (Metres) | Alarm Type | Weight (Grams) | Boxed weight (Grams) | Power Consumption | [6 empty] | Colour | Inlets | Outlets | Sound Db(A) | EAN Code/s | HS Code | Warranty | WEEE | MOQ's | Pump Medium | Run Dry | Valveless | Self Priming | Pump Technology | Sensing compatability | Ideal for | Approvals | [6 empty] | Compliance | Brand | Manufacturer | Country of origin | Header Title | Product Description (Short) | Product Description (Long) | Key Features | Application | Unique Features |  |  |  | Webpage | Datasheet | User Manual | Schematic | Product Pictures
|  |  |  | Flow (Litres/Hour) | Head (Metres) | Lift (Metres) | Length (Millimetres) | Width (Millimetres) | Height (Millimetres) | Length (Millimetres) | Width (Millimetres) | Height (Millimetres) | [5 empty] | Voltage (V) | Frequency (Hz) | Draw (A) | Power (W) | Power (VA) | Power Factor | IPX Rating | [16 empty] | UK CA | CE | cURus | UL | Plenum | ETL | ATEX | [9 empty] | USP 1 | USP 2 | USP 3 | USP 4
MegaBlue® | Condensate Removal Pump | MegaBlue + Reservoir (FSA Pack) X87-813 | 14-50kw | 50l/h | 20m | 7m | 248mm | 58mm | 68mm | 385mm | 120mm | 110mm | 2m | 0.5m | FSA - Volt Free Relay | 976g | 1250g | 240V | 50Hz | 0.072A | 12w | 17.3VA | 0.69 | IPX4 | Blue, Black, Grey, Orange | 8MM Straight | 8MM Straight | 23db(A) | MegaBlue + Reservoir (FSA Pack) 5060194290309 | 84141025 | 3 Years | 0 | 10 | Liquid/ Condensate (Including Sediment & Bio-films) | ✅ | ✅ | ✅ | Rotary Diaphragm | Thermistor Sensor (C21-008) | Cassette, Mini-split & Split systems | ✅ | ✅ | ✅ | ❌ | ✅ | ❌ | ❌ | RoHS3 (EU Directive 2011/65/EU) | BlueDiamond Pumps | Charles Austen Pumps Ltd. | United Kingdom (England) | Robust, industrial level condensate removal pump, for large scale condensate management systems | The MegaBlue® by BlueDiamond® is a robust condensate pump engineered for large commercial HVAC systems. With patented Rotary Diaphragm Technology, it offers reliable, low-maintenance performance even in harsh, debris-filled environments. | The MegaBlue® condensate pump by BlueDiamond® is a powerful, high-capacity solution engineered for large commercial spaces and multi-system HVAC installations. The MegaBlue features our patent Rotary Diaphragm Technology, delivering exceptional reliability and minimal maintenance. Its self-priming, valveless capability easily handles debris-laden or acidic condensate, making it ideal for demanding environments. As the largest and most robust pump in the BlueDiamond® range, the MegaBlue® offers unmatched performance, durability, and efficiency in condensate removal. | • Low volume in operation – 23dB(A) • Self-priming activation, no need for siphoning devices • Unique patented Rotary Diaphragm Technology • Built for large scale commercial use • Our most powerful condensate pump from the range • Forward facing spouts for simple reservoir and drainage outlet connection | • Ideal for warehouses and commercial environments • Multiple A/C systems up to 14.0 – 50.0 KW | ENGINEERED FOR INDUSTRIAL USE The MegaBlue pump by BlueDiamond is the most robust and powerful unit in our range, specifically engineered for the most demanding applications. Utilising our advanced Rotary Diaphragm Technology, the MegaBlue is ideal for multiple HVAC system installations across warehouses, and large commercial spaces. It delivers exceptional performance and reliability, efficiently removing large volumes of condensate at a faster rate than our other pumps. | FLEXIBLE SENSING OPTIONS The MegaBlue® offers a variety of smart sensing options to suit different HVAC applications: Reservoir Sensor (X87-813): Uses advanced thermistor technology, eliminating the common failures of traditional float switches. Compact, silent, and maintenance-free, it reliably detects condensate even in demanding environments. DrainStik™ Sensor (X87-820): An ultra-compact, in-line sensor designed for direct installation in the drainpipe, offering precise condensate detection without interfering with drainage flow. Temperature Sensor (X87-814): Triggers the pump when a 5°C difference is detected between the air inlet and outlet, enabling immediate, uninterrupted condensate removal. | RELIABLE RESERVOIR SENSOR Remove the hassle of stuck float switches. Our advanced thermistor-based sensing technology detects temperature variations to accurately determine the presence of condensate in the reservoir. By responding to changes in thermal conductivity caused by condensate from the air conditioning unit, it offers excellent durability, and reliability compared to basic float switches. | FLEXIBLE INSTALLATION The MegaBlue pump offers flexible installation with the ability to be mounted in any orientation without affecting performance (8m/ 23ft away from the unit). Its forward facing spouts and versatile mounting options allow for seamless integration into tight spaces or unconventional setups, ensuring reliable operation across a wide range of HVAC applications. | https://bluediamondpump.com/megablue/ | https://bluediamondpump.com/wp-content/uploads/2025/05/MegaBlue-Datasheet-2023-UK.pdf | https://bluediamondpump.com/wp-content/uploads/2025/05/S30-194_iss_8_UK-compressed.pdf | https://bluediamondpump.com/wp-content/uploads/2025/05/Wiring-Diagrams-Mini-Maxi-Mega-UK-and-EU.pdf | https://drive.google.com/drive/folders/1ZCQA6NfkSK2-4v2aD4FZ5VZAPJ2u4DY2?usp=drive_link
|  | MegaBlue + Temperature sensor X87-814 | [7 empty] | 385mm | 120mm | 110mm |  |  | No Alarm |  | 1240g | [11 empty] | MegaBlue + Temperature sensor 5060194290323 | 84141025
|  | MegaBlue + DrainStik (FSA Pack) X87-820 | [7 empty] | 385mm | 120mm | 110mm |  |  | FSA - Volt Free Relay |  | 1300g | [11 empty] | MegaBlue + DrainStik (FSA Pack) 5060194290347 | 84141025

## ArctikBlue
Product Name | Product Category | Product code/s | Air Conditioning Unit size (Kilowatt) | Performance |  |  | Pump Dimensions (MM) (Without cable and tubing) |  |  | Pump BOXED (MM) |  |  | Power lead length (Metres) | Alarm lead length (Metres) | Alarm Type | Weight (Kilograms) | Boxed Weight (Kilograms) | Power Consumption | [8 empty] | Colour | Inlet | Outlet | Tank Capacity | Pump on/off | Alarm ON volume | Pump on/off | Alarm lead | Sound Db(A) | EAN Code/s | HS Code | Warranty | WEEE | MOQ's | Pump Medium | Run Dry | Valveless | Self Priming | Pump Technology | Sensing compatability | Ideal for | Approvals | [6 empty] | Compliance | Brand | Manufacturer | Country of origin | Header Title | Product Description (Short) | Product Description (Long) | Key Features | Application | Unique Features |  |  | Webpage | Datasheet | User Manual | Schematic | Product Pictures
|  |  |  | Flow (Litres/Hour) | Head (Metres) | Lift (Metres) | Length (Millimetres) | Width (Millimetres) | Height (Millimetres) | Length (Millimetres) | Width (Millimetres) | Height (Millimetres) | [5 empty] | Voltage (V) | Frequency (Hz) | Draw (A) | Power (W) | Power (VA) | Power Factor | Alarm Signal | Max. Alarm Rating | IPX Rating | [21 empty] | UK CA | CE | cURus | UL | Plenum | ETL | ATEX | [9 empty] | USP 1 | USP 2 | USP 3
ArctikBlue® | Refrigeration Drainage Pump | ArctikBlue X87-859 | 14-50kw | 50l/h | 20m | 7m | 455mm | 422mm | 64mm | 532mm | 451mm | 95mm | 2m | 0.5m | FSA - Volt Free Relay | 4.2Kg | 5160g | 240V | 50Hz | 0.072A | 12w | 17.3VA | 0.69 | 0 Volt Relay | 5A 240V AC | IPX4 | Polished Stainless Steel Chassis, Blue, Black, Grey, Orange | 40mm ID Push Fit Connector | 12mm OD Hose Tail Stepped | 4.1 Litres | 330ml | 3600ml | 330ml | 0.25m | 23db(A) | ArctikBlue - 5060194290507 | 84141025 | 3 Years | 0 | 4 | Liquid/ Condensate (Including Sediment & Bio-films) | ✅ | ✅ | ✅ | Rotary Diaphragm | CondenSense™ | Cassette, Mini-split & Split systems | ✅ | ✅ | ✅ | ❌ | ✅ | ❌ | ❌ | RoHS3 (EU Directive 2011/65/EU) | BlueDiamond Pumps | Charles Austen Pumps Ltd | United Kingdom (England) | The lowest profile dairy cabinet pump on the market designed for reliable refrigeration drainage | BlueDiamond’s ArctikBlue is the market’s lowest-profile drainage solution for refrigeration systems. Designed for discreet installation beneath in-store units, it features a durable stainless-steel tray and integrated dry drain channel for efficient, leak-free condensate removal. Built for long-term reliability, ArctikBlue matches the lifespan of refrigeration systems and includes a 3-year warranty. | BlueDiamond’s ArctikBlue is renowned as the lowest-profile drainage solution engineered specifically for refrigeration systems on the market. Designed for seamless installation beneath in-store refrigeration units, it maintains a clean and unobtrusive appearance without compromising performance. Constructed with a robust stainless-steel tray, the ArctikBlue Pump is built to withstand demanding environments. Its integrated dry drain channel efficiently directs condensate to the pump inlet, ensuring complete drainage and reducing the risk of leaks and biofilm build-up. For engineers seeking long-term reliability, the ArctikBlue is designed to match the operational lifespan of refrigeration systems and comes with the reassurance of our three-year warranty. | • Ultra quiet operation – 23dBA • Low profile design (63.5mm) • Dry Drain Channel for complete condensate removal • Thick gauge stainless steel tray that’s long lasting • Designed to pump Biofilms, dirt and debris • Easy installation and set-up (plug and play) | • Dairy cabinets • Large scale refrigeration systems • Fridges renowned for bio-film blockages/ challenges | PUMPS BIOFILM The ArctikBlue is specifically engineered to tackle one of the toughest drainage challenges: biofilm build-up. This thick, slime-like substance, formed by bacterial and organic growth, can quickly clog conventional dairy cabinet pumps. With its powerful valveless technology and high-performance capability, the ArctikBlue efficiently removes biofilms from the system, even under demanding conditions. Its exclusive patented RD technology, allows it to handle variable outputs of condensate and biofilm without clogging—minimising blockages and drastically reducing the need for maintenance. | DISCREET, LOW PROFILE DESIGN The ArctikBlue tray features a low-profile design, standing at just 63.5 mm (2.5″) in height, allowing for discreet installation beneath refrigeration systems without occupying valuable floor space. There are no bulky components and no need to bore into the ground. It’s engineered to offer cost-effective convenience and efficiency—particularly in environments where every inch of space counts. Despite its slim profile, the ArctikBlue is built for durability. Constructed from corrosion-resistant materials, it withstands the harsh wear and tear climate, providing long-term reliability that aligns with the lifespan of your refrigeration equipment. | DRAINAGE CHANNEL The ArctikBlue’s high-grade stainless steel tray incorporates a built-in drainage channel—an indented, gravity-fed passage that guides condensate directly towards the pump. This design ensures efficient and complete drainage, helping to prevent overspilling and maintains optimal performance of the ArctikBlue. By enhancing the natural flow of condensate, the improved channel design supports reliable, maintenance–friendly operation. | https://bluediamondpump.com/artickblue/ | https://bluediamondpump.com/wp-content/uploads/2025/05/ArtickBlue-Datasheet-2023-UK.pdf | https://bluediamondpump.com/wp-content/uploads/2025/05/ARCTIKBLUE-Installation-S30-616.pdf | https://bluediamondpump.com/wp-content/uploads/2025/05/ArtickBlue-Wiring-Diagram-UK-and-EU.pdf | https://drive.google.com/drive/folders/1zr63UK6lHj7QmnaXQuBKHicAHMjM1ju7?usp=drive_link
|  | ArctikBlue - Swap-Out-Kit - X87-861 | [7 empty] | 385mm | 120mm | 107mm |  |  | FSA - Volt Free Relay |  | 1050g | [18 empty] | ArctikBlue Swapout kit- 5060194290521 | 84141025 |  |  | 10

## MultiTank
Product Name | Product Category | Product code/s | Pump Dimensions (MM) (Without cable and tubing) |  |  | Pump BOXED (MM) |  |  | Tank Capacity | Connection lead length (Metres) | Weight (Kilograms) | Boxed Weight (Kilograms) | Colour | Inlet | Inlet | Inlet | Outlet | Connection type | EAN Code/s | HS Code | Warranty | WEEE | MOQ's | Sensing Technology | Compatible with | [5 empty] | Compliance | Brand | Manufacturer | Country of Origin | Header Title | Product Description (Short) | Product Description (Long) | Key Features | Application | Unique Features |  |  | Webpage | Datasheet | User Manual | Product Pictures
|  |  | Length (Millimetres) | Width (Millimetres) | Height (Millimetres) | Length (Millimetres) | Width (Millimetres) | Height (Millimetres) | [16 empty] | MicroBlue | MiniBlue | MiniBlue R | MaxiBlue | MegaBlue | ArctikBlue | [9 empty] | USP 1 | USP 2 | USP 3
MultiTank™ | Condensate pump sensor - Reservoir | C21-014 | 355 | 126 | 115 | 375mm | 134mm | 117mm | 1.5 Litres | N/A | 600g | 860g | Black | 20mm | 25mm | 27mm | 8mm Straight | Aux | 5060194290859 | 8414900090 | 3 Years | 0 | 12 | Thermistor sensing | ❌ | ✅ | ✅ | ✅ | ✅ | ❌ | RoHS3 (EU Directive 2011/65/EU) | BlueDiamond | Charles Austen Pumps Ltd | United Kingdom (England) | CONSOLIDATE CONDENSATE DRAINAGE LINES WITH A FLEXIBLE MULTI-LINE TANK SOLUTION | The MultiTank™ is a compact mounting accessory designed for easy integration with BlueDiamond’s MegaBlue® and MaxiBlue® pumps. Ideal for tight spaces and ceiling-mounted HVAC units, it combines up to six condensate drain lines into one collection point. With no moving parts, it offers a low-maintenance, reliable alternative to traditional float switches and tank pumps. | The MultiTank™ mounting accessory is specifically engineered for seamless integration with BlueDiamond’s MegaBlue® and MaxiBlue® condensate pumps. Designed to address spatial limitations and streamline multiple condensate drainage lines into a single collection point, the MultiTank simplifies complex HVAC installations making it particularly well-suited for ceiling-mounted units or remote locations. Capable of handling up to six independent condensate drain lines, it offers a highly efficient, low-maintenance alternative to traditional float switches and tank pumps. With no moving parts to clog or seize, the MultiTank ensures reliable, long-term performance in demanding environments. | • Ultra-quiet in operation – 23dB(A) • Anti-vibration design and rubber mounts • Compatible with our MaxiBlue and MegaBlue Pumps • Capacity for up to six condensate lines • Designed for quick installation and access for installers • Lightweight | • Mini-Split systems up to 3.5KW • Small offices • Libraries • Areas where sound suppression is a priority | THERMISTOR SENSING Thermistor sensing offers a durable and reliable solution for condensate detection, eliminating common issues associated with traditional float switches, such as clogging and sticking. This technology monitors the temperature inside the tank, and when condensate comes into contact with the sensor, the Multitank detects the change and signals the pump to activate. Unlike float switches, thermistor sensing ensures consistent performance and accuracy, making it an ideal choice for systems that require precise and dependable condensate removal. | MULTIPLE DRAINAGE LINES Specifically engineered to handle up to six condensate drainage lines, the Multitank is the ideal solution for spaces with multiple AC units totalling up to 50 kW. Designed with efficiency and versatility in mind, the Multitank supports up to six condensate lines using a single pump—offering a highly cost–effective and space–saving alternative. Its compact 1.5-litre (0.4 Gallon) tank activates the pump only when needed, helping to minimise energy consumption. This makes it an excellent choice for smaller installations where both performance and efficiency are critical. | COMPATIBLE WITH THE MAXIBLUE & MEGABLUE The Multitank is compatible with our most powerful pumps; the MaxiBlue and MegaBlue. Despite their strength, both pumps operate quietly MaxiBlue (21 dB(A) and MegaBlue at 23 dB(A), ensuring minimal disruption. Both pumps are built with our exclusively patented Rotary Diaphragm Technology, featuring run-dry protection and self-priming capabilities for reliable, long-lasting performance. | https://bluediamondpump.com/multitank/ | https://bluediamondpump.com/wp-content/uploads/2025/05/Multitank-Datasheet-2023-UK.pdf | https://bluediamondpump.com/wp-content/uploads/2025/05/S30-612_ISS_2-UK-compressed.pdf | https://drive.google.com/drive/folders/1HVRoYm289kMdwHooZQYYHMelG7wzWqqb?usp=drive_link

## Sensors
Product Name | Product Category | Product code/s | Dimensions (MM) |  |  | Tank Capacity | Connection lead length (Metres) | Weight (Kilograms) | Colour | Inlet | Outlet | Connection type | EAN Code/s | Warranty | WEEE | MOQ's | HS Codes | Sensing Technology | Compatible with | [6 empty] | Brand | Manufacturer | Country Of Origin | Header Title | Product Description (Short) | Product Description (Long) | Key Features | Application | Unique Features |  |  | Webpage | Datasheet | User Manual | Product Pictures
|  |  | Length (Millimetres) | Width (Millimetres) | Height (Millimetres) | [13 empty] | MicroBlue | MiniBlue | MiniBlue R | MaxiBlue | MaxiBlue¦V2 | MegaBlue | ArctikBlue | [8 empty] | USP 1 | USP 2 | USP 3
CondenSense™ Reservoir | Condensate pump sensor - Reservoir | C21-001 | 102mm | 31mm | 38mm | 40ml | 2m | 100g | Blue, Clear Plastic | 15mm OD | 8mm OD | Aux | 5060194291207 | 3 Years | 0 | 5 | 8414900090 | CondenSense™ | ✅ | ❌ | ❌ | ❌ | ✅ | ❌ | ❌ | BlueDiamond Pumps | Charles Austen Pumps Ltd. | United Kingdom (England) | Intelligent condensate detection for HVAC system performance and maximised pump efficiency | The new CondenSense™ reservoir uses advanced technology to detect condensate changes in HVAC systems, ensuring the pump runs only when needed for better performance and energy savings. Its compact, durable design fits any ducting kit and allows for discreet installation with the new reservoir clip. | The new CondenSense™ reservoir features precise CondenSense technology – perfect for detecting changes in condensate produced by HAVC systems. The highly accurate CondenSense technology ensures the pump operates only when needed, enhancing system performance and reducing energy waste. Its compact and durable design is compatible with any ducting kit on the market, and, when used with our newly designed reservoir clip, enables discreet and seamless installations. | • Reduces costs and cuts energy waste • Can be mounted in any ducting kit using our reservoir clip. • Self-priming activation, no need for siphoning devices • Unique CondenSense™ Technology • Plug and play set-up for quick installation • Small, compact and lightweight | • Mini-Split systems up to 3.5KW • Ideal for bedrooms • Small offices • Libraries • Areas where sound suppression is a priority | CONDENSENSE™ TECHNOLOGY No more stuck float switches and regular reservoir maintenance. Our brand new capacitive sensing is a technology detects changes in capacitance to sense the presence within the reservoir. It works by measuring the electrical charge between a sensor and condensate produced by the air conditioning unit. This new sensing technology offers higher sensitivity, durability and reliability in comparison to regular float switches and thermistors. | INTELLIGENT, ADAPTIVE EFFICIENCY Designed to manage variable condensate outputs with unmatched efficiency. The MicroBlue®’s Adaptive Efficiency, is powered by its advanced soft start technology and variable speed control. This allows the pump to adjust seamlessly to fluctuating condensate levels, ensuring optimal performance without unnecessary energy consumption. By reducing sudden surges in operation and running only as needed, the MicroBlue® not only extends its lifespan but also promotes energy efficiency. | NEW UNIVERSAL RESERVOIR CLIP The reservoir clip is a durable plastic component featuring a strong adhesive backing, designed to simplify the installation of condensate removal systems. Engineered to be universally compatible with most ducting kits, it securely fits into the elbow of many ducting kit brands, making it ideal for retrofitting into pre-existing setups. Its quick-stick application significantly reduces installation time, while its robust hold ensures the reservoir remains secure and level. This innovative clip provides a practical, time-saving solution for engineers looking to streamline maintenance or upgrade to BlueDiamond’s CondenSense technology. | https://bluediamondpump.com/condensense-reservoir/ | https://bluediamondpump.com/wp-content/uploads/2025/06/Condensense-Reservoir-Datasheet-2-pages-compressed.pdf |  | https://drive.google.com/file/d/1Dsyz_JathdqzKy8_r3yV8wfTvm5hT9ec/view?usp=drive_link
MaxiBlue® Reservoir | Condensate pump sensor - Reservoir | C21-013 | 90mm | 40mm | 30mm | 40ml | 2m | 100g | Clear Plastic | 15mm OD | 8mm OD | DIN | 5060194290293 | 3 Years | 0 | 5 | 8414900090 | Thermistor | ❌ | ❌ | ❌ | ✅ | ❌ | ❌ | ❌ | BlueDiamond Pumps | Charles Austen Pumps Ltd. | United Kingdom (England) | The reliable non-float switch option designed for reliable condensate removal and minimum maintenance - Compatible with the MaxiBlue only | The MaxiBlue Reservoir is a compact, solid-state condensate sensing unit that uses thermistor technology to reliably detect water levels without moving parts, ensuring quiet and maintenance-free operation. | The MaxiBlue Reservoir is an advanced condensate sensing module designed for use with the MaxiBlue pump. Unlike traditional float-based systems, this reservoir uses patented thermistor technology to detect the presence of condensate through temperature and conductivity changes. This solid-state design ensures consistent and silent operation, even in environments where biological buildup or debris would typically interfere with mechanical sensors. | • No moving parts; more reliable than float switches • Easily fits in tight spaces; integrates cleanly with the MaxiBlue pump • Handles biofilm and light debris without clogging or sensor drift • Built-in overflow detection capability • Activates pump efficiently as water enters the reservoir | • Air conditioning systems up to 14KW • Mini-Split • Cassette systems • Mid-range fan coil applications • Ideal for large office blocks • Conference rooms • Retail and commercial areas • High-humidity environments | SMART CONDENSATE MANAGEMENT Thermistor sensing Reservoir sets itself apart with solid-state thermistor sensing technology that eliminates the common failures of traditional float switches. Detecting the presence of condensate its compact, silent it offers maintenance-free reliability in even the most demanding HVAC environments. By combining smart sensing with Rotary Diaphragm technology the reservoir ensures efficient condensate management with minimal maintenance making it the ideal choice for modern, space-conscious installations.. | N/A | N/A | N/A | N/A | https://bluediamondpump.com/wp-content/uploads/2025/05/S30-194_iss_8_UK-compressed.pdf | https://drive.google.com/file/d/10R5XBlvv_-RmtYEccayTfiAOv_b-OfNy/view?usp=sharing
MegaBlue® Reservoir | Condensate pump sensor - Reservoir | C21-008 | 70mm | 60mm | 45mm | 60ml | 2m | 100g | Clear Plastic | 15mm OD | 8mm OD | DIN | 5060194290385 | 3 Years | 0 | 5 | 8414900090 | Thermistor | ❌ | ❌ | ❌ | ❌ | ❌ | ✅ | ❌ | BlueDiamond Pumps | Charles Austen Pumps Ltd. | United Kingdom (England) | The durable non-float switch option designed for reliable condensate removal and minimum maintenance - Compatible with the MegaBlue only | High-capacity condensate reservoir designed for use with MegaBlue for high-output systems. | The MegaBlue Reservoir is a robust, high-capacity water reservoir engineered to complement BlueDiamond’s range of pumps. Built to handle larger volumes of condensate, it ensures smooth, continuous operation even in demanding HVAC systems. Its durable construction and compatibility with BlueDiamond accessories make it the ideal choice for commercial or high-output air conditioning units where volume and reliability matter. | • Designed for use with BlueDiamond pump systems • High-capacity chamber for larger condensate volumes • Supports continuous or high-demand HVAC applications • Durable, leak-resistant construction • Easy to integrate into existing pump setups • Optimises pump efficiency by regulating condensate input | • Ideal for warehouses and commercial environments • Multiple A/C systems up to 14.0 – 50.0 KW | ROBUST CONDENSATE MANAGEMENT Engineered for high-demand HVAC systems, the MegaBlue Reservoir maximises pump efficiency by providing consistent, controlled condensate flow to prevent system overload. | N/A | N/A | N/A | N/A | https://bluediamondpump.com/wp-content/uploads/2025/05/S30-194_iss_8_UK-compressed.pdf | https://drive.google.com/file/d/1H6ffy4y2_3wQ0q1TNeOnDE0bQOWBNTG-/view?usp=drive_link
Temperature Sensor | Condensate pump sensor - hot and cold detector | S12-002 | N/A | N/A | N/A | N/A | 2m | 50g | Black, Red and Blue | N/A | N/A | DIN | 5060194290392 | 3 Years | 0 | 5 | 8414900090 | Thermistor | ❌ | ✅ | ✅ | ✅ | ❌ | ✅ | ❌ | BlueDiamond Pumps | Charles Austen Pumps Ltd. | United Kingdom (England) | Smart temperature detection for automatic pump activation during condensate production | Smart sensor that detects environmental temperature shifts (5°C difference) to trigger condensate pump activation. | BlueDiamond’s Temperature Sensor provides intelligent monitoring of ambient or surface temperatures to accurately detect the onset of cooling cycles. Once a change is detected (5°C difference), it triggers immediate pump activation to manage condensate from the moment your air conditioning unit powers on. This ensures efficient and uninterrupted condensate removal, minimising the risk of overflow and system strain. | • Detects temperature changes to initiate pump cycles • Automatically starts pump when AC unit powers on • Ensures prompt and uninterrupted condensate removal • Reduces risk of overflow and pump lag • Compact and reliable for long-term performance • Ideal for integration into temperature-sensitive environments | • Mini-Split systems between 8-50KW • Use with MiniBlue, MaxiBlue and MegaBlue pump • Perfect alternative where space for a reservoir is not an option | THE SMART RESERVOIR ALTERNATIVE Activates your pump the moment there is a 5°C difference in room temperature. Ensuring immediate, uninterrupted condensate removal with zero delay. One sensor lead is positioned at the air outlet and the other sensor at the air inlet. | N/A | N/A | N/A | N/A | https://bluediamondpump.com/wp-content/uploads/2025/05/S30-194_iss_8_UK-compressed.pdf | https://drive.google.com/file/d/1mfg13Ig-HdoHu7D3FJDOQ3NETFIymfPm/view?usp=drive_link
DrainStik® | Condensate pump sensor - Reservoir | S12-004 | N/A | N/A | N/A | N/A | 2m | 10g | Black, Clear Plastic | N/A | N/A | DIN | 5060194290866 | 3 Years | 0 | 5 | 8414900090 | Thermistor | ❌ | ❌ | ❌ | ✅ | ❌ | ✅ | ❌ | BlueDiamond Pumps | Charles Austen Pumps Ltd. | United Kingdom (England) | Targeted condensate management at drainpipe level | A compact, easy-to-install in-line sensor for detecting condensate presence directly at the drainpipe. | The DrainStik® is a discreet, plug-and-play in-line condensate sensor designed to sit directly in the drainpipe, detecting the presence of condensate with high accuracy. Its smart integration enables precise pump activation only when needed, improving efficiency while preventing overflow. Ideal for space-limited applications, DrainStik® offers reliable performance without disrupting the flow path. | • Senses condensate directly within the drainpipe • Compact, low-profile design for tight installations • Enables smart, sensor-driven pump activation • Prevents overflow by detecting real-time condensate presence • Quick and easy to install with minimal disruption • Ideal for ductless systems and concealed spaces | • Mini-Split systems between 8-50KW • Use with MiniBlue, MaxiBlue and MegaBlue pump • Perfect alternative where space for a reservoir is not an option | COMPACT AND EASY TO INSTALL The only ultra-compact in-line sensor designed for seamless integration directly into the drainpipe, delivering precise condensate detection without disrupting drainage outlets. | N/A | N/A | N/A | N/A | https://bluediamondpump.com/wp-content/uploads/2025/05/S30-194_iss_8_UK-compressed.pdf | https://drive.google.com/file/d/10R5XBlvv_-RmtYEccayTfiAOv_b-OfNy/view?usp=sharing
CR Plug | Condensate pump sensor - Continuous running plug | P02-048 | 45mm | 14mm | 14mm | N/A | 2m | 10g | Black | N/A | N/A | DIN | 5060194290880 | 3 Years | 0 | 5 | 8414900090 | Electronic | ❌ | ✅ | ✅ | ✅ | ❌ | ✅ | ❌ | BlueDiamond Pumps | Charles Austen Pumps Ltd. | United Kingdom (England) | Instant pump response for uninterrupted condensate removal | Allows continuous operation of selected BlueDiamond pumps, ideal for high-demand or always-on systems. | The CR Plug (Continuous Running Plug) enables your BlueDiamond pump to operate continuously, independent of sensor input. This is especially useful in systems where condensate is produced constantly, or where uninterrupted drainage is critical. Designed for quick installation, the CR Plug ensures a consistent, proactive approach to condensate removal in high-throughput environments. | • Enables continuous pump operation without sensor input • Ideal for systems with constant condensate production • Simple plug-and-play installation • Ensures proactive, uninterrupted condensate drainage • Recommended for high-throughput or mission-critical systems • Compatible with selected BlueDiamond pump range | • Any A/C system between 8-50KW • Use with MiniBlue, MaxiBlue and MegaBlue pump • Perfect alternative where space for a reservoir is not an option | MOST SIMPLIFIED SENSING SOLUTION Transforms your BlueDiamond pump into a continuously running system, delivering constant drainage performance for environments with nonstop condensate production the moment your HVAC system is turned on. | N/A | N/A | N/A | N/A | https://bluediamondpump.com/wp-content/uploads/2025/05/S30-194_iss_8_UK-compressed.pdf | https://drive.google.com/file/d/1tzdfEuTBsi8lC928PLw0ByIPfAariWSL/view?usp=drive_link